# North Utilities - CHWP-2 Alignment and Baseplate Report

Evidence window: 2026-08-03 through 2026-08-16. Asset scope: CHWP-2, M-CHWP-2, and CPL-CHWP-2 pump train.

# 1. Alignment source hierarchy

The laser alignment record controls measured coupling alignment. Site tolerance is a screening value only. OEM tolerance controls final acceptance for the pump train.

# 2. Laser alignment readings

| record_id | stage | vertical_offset_mm | vertical_angular_mm_per_100 | horizontal_offset_mm | horizontal_angular_mm_per_100 | site_result | oem_result | notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ALIGN-001 | rough pre-shim | +0.26 | -0.18 | +0.34 | -0.22 | FAIL | FAIL | initial after spider replacement |
| ALIGN-006 | after vertical shim | +0.08 | -0.07 | +0.28 | -0.19 | FAIL | FAIL | vertical improved |
| ALIGN-011 | final contractor reading | +0.04 | -0.03 | +0.10 | -0.07 | PASS | FAIL | site pass but OEM fail |
| ALIGN-012 | site tolerance sheet | limit 0.13 | limit 0.10 | limit 0.13 | limit 0.10 | PASS basis | not controlling | general site values |
| ALIGN-013 | OEM tolerance line | limit 0.06 | limit 0.05 | limit 0.06 | limit 0.05 | not used by contractor | controlling | OEM tighter limits |

Resolved conclusion: the final horizontal offset of +0.10 mm and final horizontal angular of -0.07 mm per 100 mm fail the OEM tolerance. The pump train must not be closed on the site-pass label.

# 3. Soft foot, baseplate, and pipe strain

| record_id | item | evidence | status | trace_note |
| --- | --- | --- | --- | --- |
| ALIGN-020 | soft foot pre-shim | 0.11 mm feeler at motor front inboard foot | unresolved | loosen-and-repeat verification missing after horizontal move |
| ALIGN-024 | shim change | 0.05 mm shim installed under motor front inboard foot | partial | shim installed but repeat test not recorded |
| ALIGN-031 | pipe strain check | loosening suction spool changed horizontal offset by +0.06 mm | unresolved | pipe strain likely |
| ALIGN-040 | baseplate observation | 85 mm hairline crack at pump north plinth corner | unresolved | exceeds local report threshold of 50 mm |
| ALIGN-042 | support clamp note | suction support clamp tightened after final reading | unresolved | no repeat laser reading recorded |
| ALIGN-043 | kit return | laser kit returned to tool crib at 2026-08-08 16:10 | unresolved | no later alignment record in evidence window |

# 4. LOTO references in alignment work

| record_id | wo_id | loto_permit | finding |
| --- | --- | --- | --- |
| ALIGN-050 | WO-92034 | LOTO-4118 | permit lacks verification signature |
| ALIGN-051 | WO-92034 | LOTO-4118 | scope covered pump, motor, coupling; CMMS asset entered as MTR-402 only |

# 5. Required reconciliation treatment

Classify alignment as OEM FAIL until a repeat laser reading verifies horizontal offset and angular tolerance after pipe strain isolation.

Classify coupling spider replacement separately from alignment acceptance.

Keep soft-foot verification and baseplate crack open until documented.