## Source_Index
source_id | sheet_or_record | description | source_file | trace_note
PFR-SI | Source_Index | Workbook source index | HOSP_CHW_pump_curve_and_field_readings.xlsx | Input workbook
CURVE50 | Pump_Curve_50Hz | CHWP-2 OEM curve at 50 Hz | HOSP_CHW_pump_curve_and_field_readings.xlsx | n = local pump curve
CURVE47 | Pump_Curve_47Hz | CHWP-2 reference curve at 47 Hz | HOSP_CHW_pump_curve_and_field_readings.xlsx | derived by vendor field sheet
FIELD | Field_Readings | field pressure, flow, temperature readings | HOSP_CHW_pump_curve_and_field_readings.xlsx | compare against BAS
SCALE | Flow_Scaling_Check | pre-correction BAS scale mismatch | HOSP_CHW_pump_curve_and_field_readings.xlsx | 0-2400 vs 0-1800 gpm

## Pump_Curve_50Hz
curve_id | hz | flow_gpm | head_ft | efficiency_pct | notes
50Hz-01 | 50 | 900 | 112 | 73 | reference curve
50Hz-02 | 50 | 1100 | 106 | 75 | reference curve
50Hz-03 | 50 | 1300 | 98 | 77 | reference curve
50Hz-04 | 50 | 1500 | 86 | 75 | reference curve
50Hz-05 | 50 | 1700 | 71 | 73 | reference curve

## Pump_Curve_47Hz
curve_id | hz | flow_gpm | head_ft | efficiency_pct | notes
47Hz-01 | 47 | 846 | 99 | 72.5 | reference curve
47Hz-02 | 47 | 1034 | 94 | 74.3 | reference curve
47Hz-03 | 47 | 1222 | 87 | 76.2 | reference curve
47Hz-04 | 47 | 1410 | 77 | 75.9 | reference curve
47Hz-05 | 47 | 1598 | 63 | 74 | reference curve

## Field_Readings
reading_id | timestamp | hz | flow_tag | flow_gpm_displayed | ultrasonic_gpm | suction_psi | discharge_psi | chw_supply_f | chw_return_f | notes
PFR-001 | 2026-08-03 07:00 | 47 | BAS pre-correction | 1620 | 1215 | 10.8 | 52.2 | 44 | 53.2 | pre scale issue
PFR-002 | 2026-08-05 08:00 | 50 | BAS pre-correction | 1760 | 1320 | 11.4 | 59 | 44.5 | 53.6 | vibration alarm
PFR-003 | 2026-08-07 13:40 | 50 | BAS pre-correction | 1715 | 1285 | 11 | 58.1 | 45.2 | 52 | after disputed seal
PFR-004 | 2026-08-08 15:40 | 47 | BAS pre-correction | 1550 | 1165 | 10.6 | 50.8 | 45.6 | 51.9 | after alignment
PFR-005 | 2026-08-10 12:00 | 50 | BAS pre-correction | 1690 | 1268 | 10.7 | 57.4 | 45.4 | 51.7 | HX DP high
PFR-006 | 2026-08-12 09:45 | 50 | BAS post-correction | 1360 | 1375 | 11.8 | 62.7 | 44.7 | 54.5 | scaling corrected
PFR-007 | 2026-08-15 15:10 | 50 | BAS post-correction | 1465 | 1472 | 12 | 64.1 | 44.1 | 54.3 | post strainer clean
PFR-008 | 2026-08-16 07:30 | 47 | BAS post-correction | 1190 | 1198 | 11.1 | 54.4 | 45.3 | 51.4 | low delta T and trip

## Flow_Scaling_Check
reading_id | displayed_gpm | ultrasonic_gpm | expected_rescale | rescaled_gpm | error_pct | verdict
PFR-001 | 1620 | 1215
PFR-002 | 1760 | 1320
PFR-003 | 1715 | 1285
PFR-004 | 1550 | 1165
PFR-005 | 1690 | 1268
PFR-006 | 1360 | 1375

## TDH_Calculations
reading_id | suction_psi | discharge_psi | elevation_ft | tdh_ft | formula_note
PFR-001 | 10.8 | 52.2 | 3 |  | TDH=(D-S)*2.31+3.0
PFR-002 | 11.4 | 59 | 3 |  | TDH=(D-S)*2.31+3.0
PFR-003 | 11 | 58.1 | 3 |  | TDH=(D-S)*2.31+3.0
PFR-004 | 10.6 | 50.8 | 3 |  | TDH=(D-S)*2.31+3.0
PFR-005 | 10.7 | 57.4 | 3 |  | TDH=(D-S)*2.31+3.0
PFR-006 | 11.8 | 62.7 | 3 |  | TDH=(D-S)*2.31+3.0
PFR-007 | 12 | 64.1 | 3 |  | TDH=(D-S)*2.31+3.0
PFR-008 | 11.1 | 54.4 | 3 |  | TDH=(D-S)*2.31+3.0

## DeltaT_Check
reading_id | supply_f | return_f | delta_t_f | low_delta_t_flag | note
PFR-001 | 44 | 53.2 |  |  | pre scale issue
PFR-002 | 44.5 | 53.6 |  |  | vibration alarm
PFR-003 | 45.2 | 52 |  |  | after disputed seal
PFR-004 | 45.6 | 51.9 |  |  | after alignment
PFR-005 | 45.4 | 51.7 |  |  | HX DP high
PFR-006 | 44.7 | 54.5 |  |  | scaling corrected
PFR-007 | 44.1 | 54.3 |  |  | post strainer clean
PFR-008 | 45.3 | 51.4 |  |  | low delta T and trip

## Reference_Notes
reference_name | url | use_in_task
OSHA 29 CFR 1910.147 | https://www.osha.gov/laws-regs/regulations/standardnumber/1910/1910.147 | lockout/tagout control of hazardous energy
DOE O&M Best Practices Guide | https://www.energy.gov/sites/prod/files/2020/04/f74/omguide_complete_w-eo-disclaimer.pdf | maintenance interpretation and building systems
DOE FEMP BMP #10 Cooling Tower Management | https://www.energy.gov/cmei/femp/best-management-practice-10-cooling-tower-management | cooling tower cycles, blowdown, conductivity, basin management